## Load_G2
Load_G2 avr_ESST1a
Tr | 0.015 | [s] | Measurement Delay
Tb | 0.5 | [s] | Filter 1st Delay Time Constant
Tc | 0.1 | [s] | Filter 1st Derivative Time Constant
Tb1 | 0.5 | [s] | Filter 2nd Delay Time Constant
Tc1 | 1 | [s] | Filter 2nd Derivative Time Constant
Ka | 150 | [pu] | Controller Gain
Ta | 0.05 | [s] | Controller Time Constant
Kc | 0.01 | [pu] | Current Limiter Factor
Kf | 0.01 | [pu] | Stabilization Path Gain
Tf | 1.2 | [s] | Stabilization Path Time Constant
Klr | 1 | [pu] | Current Input Factor
Ilr | 1 | [pu] | Current Input Referece
Vos | 1 | [1,2] | PSS Input Selector
Vel | 2 | [1,2,3] | Uel Input Selector
Vimin | -0.25 | [pu] | Controller Input Minimum
Vamin | -5 | [pu] | Controller Minimum Output
Vrmin | -4 | [pu] | Exciter Minimum Output
Vimax | 0.15 | [pu] | Controller Input Maximum
Vamax | 5 | [pu] | Controller Maximum Output
Vrmax | 4 | [pu] | Exciter Maximum Output

## G10
G10 AVR |  |  |  | TGOV1
Tr | 0.015 | [s] | Measurement Delay | T3 | 2 | [pu] | Turbine Delay Time Constant
Tb | 0.5 | [s] | Filter 1st Delay Time Constant | T2 | 1 | [pu] | Turbine Derivative Time Constant
Tc | 0.1 | [s] | Filter 1st Derivative Time Constant | At | 1 | [pu] | Turbine power coefficient
Tb1 | 0.5 | [s] | Filter 2nd Delay Time Constant | Dt | 0 | [pu] | Frictional Losses Factor
Tc1 | 1 | [s] | Filter 2nd Derivative Time Constant | R | 0.05 | [pu] | Controller Droop
Ka | 150 | [pu] | Controller Gain | T1 | 0.2 | [s] | Governor Time Constant
Ta | 0.05 | [s] | Controller Time Constant | PN | 0 | [Mw] | Turbine Rated Power(=0->PN=Pgnn)
Kc | 0.01 | [pu] | Current Limiter Factor | Vmin | 0 | [pu] | Minimum Gate Limit
Kf | 0.01 | [pu] | Stabilization Path Gain | Vmax | 1 | [pu] | Maximum Gate Limit
Tf | 1.2 | [s] | Stabilization Path Time Constant
Klr | 1 | [pu] | Current Input Factor
Ilr | 1 | [pu] | Current Input Referece
Vos | 1 | [1,2] | PSS Input Selector | STAB1
Vel | 2 | [1,2,3] | Uel Input Selector | K | 313.5984 | [pu] | Stabilizer Gain
Vimin | -0.25 | [pu] | Controller Input Minimum | T | 11.0032 | [s] | Washout integrate time constant
Vamin | -5 | [pu] | Controller Minimum Output | T2 | 1.9537 | [s] | Second Lead/Lag derivative time constant
Vrmin | -4 | [pu] | Exciter Minimum Output | T4 | 0.77283 | [s] | Second Lead/Lag delay time constant
Vimax | 0.15 | [pu] | Controller Input Maximum | T1 | 1.7377 | [s] | First Lead/Lag derivative time constant
Vamax | 5 | [pu] | Controller Maximum Output | T3 | 0.8024 | [s] | First Lead/Lag delay time constant
Vrmax | 4 | [pu] | Exciter Maximum Output | HLIM | 0.03 | [pu] | Signal pss maximum

## G3
avr_ESST1A |  |  |  | TGOV1
Tr | 0.015 | [s] | Measurement Delay | T3 | 2 | [pu] | Turbine Delay Time Constant
Tb | 0.5 | [s] | Filter 1st Delay Time Constant | T2 | 1 | [pu] | Turbine Derivative Time Constant
Tc | 0.1 | [s] | Filter 1st Derivative Time Constant | At | 1 | [pu] | Turbine power coefficient
Tb1 | 0.5 | [s] | Filter 2nd Delay Time Constant | Dt | 0 | [pu] | Frictional Losses Factor
Tc1 | 1 | [s] | Filter 2nd Derivative Time Constant | R | 0.05 | [pu] | Controller Droop
Ka | 150 | [pu] | Controller Gain | T1 | 0.2 | [s] | Governor Time Constant
Ta | 0.05 | [s] | Controller Time Constant | PN | 0 | [Mw] | Turbine Rated Power(=0->PN=Pgnn)
Kc | 0.01 | [pu] | Current Limiter Factor | Vmin | 0 | [pu] | Minimum Gate Limit
Kf | 0.01 | [pu] | Stabilization Path Gain | Vmax | 1 | [pu] | Maximum Gate Limit
Tf | 1.2 | [s] | Stabilization Path Time Constant
Klr | 1 | [pu] | Current Input Factor
Ilr | 1 | [pu] | Current Input Referece
Vos | 1 | [1,2] | PSS Input Selector
Vel | 2 | [1,2,3] | Uel Input Selector
Vimin | -0.25 | [pu] | Controller Input Minimum | STAB1
Vamin | -5 | [pu] | Controller Minimum Output | K | 303.673 | [pu] | Stabilizer Gain
Vrmin | -4 | [pu] | Exciter Minimum Output | T | 8.1788 | [s] | Washout integrate time constant
Vimax | 0.15 | [pu] | Controller Input Maximum | T2 | 1.2901 | [s] | Second Lead/Lag derivative time constant
Vamax | 5 | [pu] | Controller Maximum Output | T4 | 1.9088 | [s] | Second Lead/Lag delay time constant
Vrmax | 4 | [pu] | Exciter Maximum Output | T1 | 1.7468 | [s] | First Lead/Lag derivative time constant
|  |  |  | T3 | 1.638 | [s] | First Lead/Lag delay time constant
|  |  |  | HLIM | 0.03 | [pu] | Signal pss maximum

## G4
avr |  |  |  | TGOV5
Tr | 0.015 | [s] | Measurement Delay | K | 10 | [p.u.] | Controller Gain
Tb | 0.5 | [s] | Filter 1st Delay Time Constant | T1 | 0.2 | [s] | Governor Time Constant
Tc | 0.1 | [s] | Filter 1st Derivative Time Constant | T2 | 1 | [s] | Governor Derivative Time Constant
Tb1 | 0.5 | [s] | Filter 2nd Delay Time Constant | T3 | 0.6 | [s] | Servo Time Constant
Tc1 | 1 | [s] | Filter 2nd Derivative Time Constant | K1 | 0.3 | [p.u.] | High Pressure Turbine Factor
Ka | 150 | [pu] | Controller Gain | K2 | 0 | [p.u.] | High Pressure Turbine Factor
Ta | 0.05 | [s] | Controller Time Constant | T5 | 0.5 | [s] | Intermediate Pressure Turbine Time Constant
Kc | 0.01 | [pu] | Current Limiter Factor | K3 | 0.25 | [p.u.] | Intermediate Pressure Turbine Factor
Kf | 0.01 | [pu] | Stabilization Path Gain | K4 | 0 | [p.u.] | Intermediate Pressure Turbine Factor
Tf | 1.2 | [s] | Stabilization Path Time Constant | T6 | 0.8 | [s] | Medium Pressure Turbine Time Constant
Klr | 1 | [pu] | Current Input Factor | K5 | 0.3 | [p.u.] | Medium Pressure Turbine Factor
Ilr | 1 | [pu] | Current Input Referece | K6 | 0 | [p.u.] | Medium Pressure Turbine Factor
Vos | 1 | [1,2] | PSS Input Selector | T4 | 0.6 | [s] | High Pressure Turbine Time Constant
Vel | 2 | [1,2,3] | Uel Input Selector | T7 | 1 | [s] | Low Pressure Turbine Time Constant
Vimin | -0.25 | [pu] | Controller Input Minimum | K7 | 0.15 | [p.u.] | Low Pressure Turbine Factor
Vamin | -5 | [pu] | Controller Minimum Output | K8 | 0 | [p.u.] | Low Pressure Turbine Factor
Vrmin | -4 | [pu] | Exciter Minimum Output | PNhp | 0 | [MW] | HP Turbine Rated Power(=0->PNhp=PgnnHp)
Vimax | 0.15 | [pu] | Controller Input Maximum | PNlp | 0 | [MW] | LP Turbine Rated Power(=0->PNlp=Pgnnlp)
Vamax | 5 | [pu] | Controller Maximum Output | B | 0.05 | [pu] | The frequency bias for load reference control.
Vrmax | 4 | [pu] | Exciter Maximum Output | K13 | 0.02 | [-] | The gain between MW demand and pressure set point.
|  |  |  | K12 | 0.02 | [-] | The gain for pressure error bias.
STAB2 |  |  |  | Kmw | 1 | [-] | The gain of the MW transducer (0 or 1).
K | 235.8964 | [pu] | Stabilizer Gain | Tmw | 10 | [s] | The MW transducer time constant
T | 5.261 | [s] | Washout integrate time constant | K14 | 5 | [-] | Inverse of load reference servomotor time constant (= 0.0 if load reference does not change).
T2 | 0.01 | [s] | Second Lead/Lag derivative time constant | Kl | 1 | [-] | The feedback gain from the load reference (0 or 1).
T4 | 0.45938 | [s] | Second Lead/Lag delay time constant | Dpe | 0.001 | [pu of Pres] | The deadband in the pressure error signal for load reference control
T1 | 2.0622 | [s] | First Lead/Lag derivative time constant | Ki | 0.02 | [pu] | The controller integral gain.
T3 | 0.62604 | [s] | First Lead/Lag delay time constant | Ti | 90 | [s] | The controller proportional lead time constant
switchselect | 1 |  |  | Tr | 60 | [s] | The controller rate lead time constant
HLIM | 0.03 | [pu] | Signal pss maximum | Tri | 6 | [s] | The inherent lag associated with lead TR
|  |  |  | K9 | 0 | [-] | The adjustment to the pressure drop coefficient as a function of drum pressure.
|  |  |  | Cb | 750 | [s] | The boiler storage time constant
|  |  |  | Tf | 25 | [s] | The fuel and air system time constant
|  |  |  | Tw | 7 | [s] | Fuel flow time constant
|  |  |  | Td | 60 | [s] | The time delay in the fuel supply system
|  |  |  | K11 | 0.1 | [-] | The gain of anticipation signal from load demand.
|  |  |  | K10 | 0.1 | [-] | The gain of anticipation signal from main stream flow.
|  |  |  | C1 | 0.2 | [-] | The pressure drop coefficient.
|  |  |  | Psp | 1 | [pu] | The initial throttle pressure set point.
|  |  |  | C2 | 0 | [-] | The gain for the pressure error bias.
|  |  |  | C3 | 1 | [-] | The adjustment to the pressure set point.
|  |  |  | Uc | -0.3 | [p.u./s] | Valve Closing Time
|  |  |  | Vmin | 0 | [p.u.] | Minimum Gate Limit
|  |  |  | Rmin | -0.3 | [pu/s] | The load reference negative rate of change limit
|  |  |  | Lmin | 0.2 | [pu] | The minimum load reference.
|  |  |  | Cmin | 0.1 | [pu] | The minimum controller output.
|  |  |  | Uo | 0.3 | [p.u./s] | Valve Opening Time
|  |  |  | Vmax | 1 | [p.u.] | Maximum Gate Limit
|  |  |  | Rmax | 0.3 | [pu/s] | The load reference positive rate of change limit
|  |  |  | Lmax | 1 | [pu] | The maximum load reference.
|  |  |  | Cmax | 1.2 | [pu] | The maximum controller output.

## G5
avr |  |  |  | TGOV1
Tr | 0.015 | [s] | Measurement Delay | T3 | 2 | [pu] | Turbine Delay Time Constant
Tb | 0.5 | [s] | Filter 1st Delay Time Constant | T2 | 1 | [pu] | Turbine Derivative Time Constant
Tc | 0.1 | [s] | Filter 1st Derivative Time Constant | At | 1 | [pu] | Turbine power coefficient
Tb1 | 0.5 | [s] | Filter 2nd Delay Time Constant | Dt | 0 | [pu] | Frictional Losses Factor
Tc1 | 1 | [s] | Filter 2nd Derivative Time Constant | R | 0.05 | [pu] | Controller Droop
Ka | 150 | [pu] | Controller Gain | T1 | 0.2 | [s] | Governor Time Constant
Ta | 0.05 | [s] | Controller Time Constant | PN | 0 | [Mw] | Turbine Rated Power(=0->PN=Pgnn)
Kc | 0.01 | [pu] | Current Limiter Factor | Vmin | 0 | [pu] | Minimum Gate Limit
Kf | 0.01 | [pu] | Stabilization Path Gain | Vmax | 1 | [pu] | Maximum Gate Limit
Tf | 1.2 | [s] | Stabilization Path Time Constant
Klr | 1 | [pu] | Current Input Factor
Ilr | 1 | [pu] | Current Input Referece | STAB2
Vos | 1 | [1,2] | PSS Input Selector | K | 195.745 | [pu] | Stabilizer Gain
Vel | 2 | [1,2,3] | Uel Input Selector | T | 7.041 | [s] | Washout integrate time constant
Vimin | -0.25 | [pu] | Controller Input Minimum | T2 | 2.5922 | [s] | Second Lead/Lag derivative time constant
Vamin | -5 | [pu] | Controller Minimum Output | T4 | 0.90029 | [s] | Second Lead/Lag delay time constant
Vrmin | -4 | [pu] | Exciter Minimum Output | T1 | 1.632 | [s] | First Lead/Lag derivative time constant
Vimax | 0.15 | [pu] | Controller Input Maximum | T3 | 0.77268 | [s] | First Lead/Lag delay time constant
Vamax | 5 | [pu] | Controller Maximum Output | switchselect | 1
Vrmax | 4 | [pu] | Exciter Maximum Output | HLIM | 0.03 | [pu] | Signal pss maximum

## G6
avr |  |  |  | TGOV1
Tr | 0.015 | [s] | Measurement Delay | T3 | 2 | [pu] | Turbine Delay Time Constant
Tb | 0.5 | [s] | Filter 1st Delay Time Constant | T2 | 1 | [pu] | Turbine Derivative Time Constant
Tc | 0.1 | [s] | Filter 1st Derivative Time Constant | At | 1 | [pu] | Turbine power coefficient
Tb1 | 0.5 | [s] | Filter 2nd Delay Time Constant | Dt | 0 | [pu] | Frictional Losses Factor
Tc1 | 1 | [s] | Filter 2nd Derivative Time Constant | R | 0.05 | [pu] | Controller Droop
Ka | 150 | [pu] | Controller Gain | T1 | 0.2 | [s] | Governor Time Constant
Ta | 0.05 | [s] | Controller Time Constant | PN | 0 | [Mw] | Turbine Rated Power(=0->PN=Pgnn)
Kc | 0.01 | [pu] | Current Limiter Factor | Vmin | 0 | [pu] | Minimum Gate Limit
Kf | 0.01 | [pu] | Stabilization Path Gain | Vmax | 1 | [pu] | Maximum Gate Limit
Tf | 1.2 | [s] | Stabilization Path Time Constant
Klr | 1 | [pu] | Current Input Factor
Ilr | 1 | [pu] | Current Input Referece | STAB2
Vos | 1 | [1,2] | PSS Input Selector | K | 178.1284 | [pu] | Stabilizer Gain
Vel | 2 | [1,2,3] | Uel Input Selector | T | 5.1665 | [s] | Washout integrate time constant
Vimin | -0.25 | [pu] | Controller Input Minimum | T2 | 2.7868 | [s] | Second Lead/Lag derivative time constant
Vamin | -5 | [pu] | Controller Minimum Output | T4 | 1.5845 | [s] | Second Lead/Lag delay time constant
Vrmin | -4 | [pu] | Exciter Minimum Output | T1 | 2.5244 | [s] | First Lead/Lag derivative time constant
Vimax | 0.15 | [pu] | Controller Input Maximum | T3 | 1.1039 | [s] | First Lead/Lag delay time constant
Vamax | 5 | [pu] | Controller Maximum Output | switchselect | 1
Vrmax | 4 | [pu] | Exciter Maximum Output | HLIM | 0.03 | [pu] | Signal pss maximum

## G7
avr |  |  |  | IEEEG1
Tr | 0.015 | [s] | Measurement Delay | K | 5 | [p.u.] | Controller Gain
Tb | 0.5 | [s] | Filter 1st Delay Time Constant | T1 | 0.2 | [s] | Governor Time Constant
Tc | 0.1 | [s] | Filter 1st Derivative Time Constant | T2 | 1 | [s] | Governor Derivative Time Constant
Tb1 | 0.5 | [s] | Filter 2nd Delay Time Constant | T3 | 0.6 | [s] | Servo Time Constant
Tc1 | 1 | [s] | Filter 2nd Derivative Time Constant | K1 | 0.3 | [p.u.] | High Pressure Turbine Factor
Ka | 150 | [pu] | Controller Gain | K2 | 0 | [p.u.] | High Pressure Turbine Factor
Ta | 0.05 | [s] | Controller Time Constant | T5 | 0.5 | [s] | Intermediate Pressure Turbine Time Constant
Kc | 0.01 | [pu] | Current Limiter Factor | K3 | 0.25 | [p.u.] | Intermediate Pressure Turbine Factor
Kf | 0.01 | [pu] | Stabilization Path Gain | K4 | 0 | [p.u.] | Intermediate Pressure Turbine Factor
Tf | 1.2 | [s] | Stabilization Path Time Constant | T6 | 0.8 | [s] | Medium Pressure Turbine Time Constant
Klr | 1 | [pu] | Current Input Factor | K5 | 0.3 | [p.u.] | Medium Pressure Turbine Factor
Ilr | 1 | [pu] | Current Input Referece | K6 | 0 | [p.u.] | Medium Pressure Turbine Factor
Vos | 1 | [1,2] | PSS Input Selector | T4 | 0.6 | [s] | High Pressure Turbine Time Constant
Vel | 2 | [1,2,3] | Uel Input Selector | T7 | 1 | [s] | Low Pressure Turbine Time Constant
Vimin | -0.25 | [pu] | Controller Input Minimum | K7 | 0.15 | [p.u.] | Low Pressure Turbine Factor
Vamin | -5 | [pu] | Controller Minimum Output | K8 | 0 | [p.u.] | Low Pressure Turbine Factor
Vrmin | -4 | [pu] | Exciter Minimum Output | PNhp | 0 | [MW] | HP Turbine Rated Power(=0->PNhp=PgnnHp)
Vimax | 0.15 | [pu] | Controller Input Maximum | PNlp | 0 | [MW] | LP Turbine Rated Power(=0->PNlp=Pgnnlp)
Vamax | 5 | [pu] | Controller Maximum Output | Uc | -0.3 | [p.u./s] | Valve Closing Time
Vrmax | 4 | [pu] | Exciter Maximum Output | Pmin | 0 | [p.u.] | Minimum Gate Limit
|  |  |  | Uo | 0.3 | [p.u./s] | Valve Opening Time
|  |  |  | Pmax | 1 | [p.u.] | Maximum Gate Limit

## G8
avr |  |  |  | TGOV1
Tr | 0.015 | [s] | Measurement Delay | T3 | 2 | [pu] | Turbine Delay Time Constant
Tb | 0.5 | [s] | Filter 1st Delay Time Constant | T2 | 1 | [pu] | Turbine Derivative Time Constant
Tc | 0.1 | [s] | Filter 1st Derivative Time Constant | At | 1 | [pu] | Turbine power coefficient
Tb1 | 0.5 | [s] | Filter 2nd Delay Time Constant | Dt | 0 | [pu] | Frictional Losses Factor
Tc1 | 1 | [s] | Filter 2nd Derivative Time Constant | R | 0.05 | [pu] | Controller Droop
Ka | 150 | [pu] | Controller Gain | T1 | 0.2 | [s] | Governor Time Constant
Ta | 0.05 | [s] | Controller Time Constant | PN | 0 | [Mw] | Turbine Rated Power(=0->PN=Pgnn)
Kc | 0.01 | [pu] | Current Limiter Factor | Vmin | 0 | [pu] | Minimum Gate Limit
Kf | 0.01 | [pu] | Stabilization Path Gain | Vmax | 1 | [pu] | Maximum Gate Limit
Tf | 1.2 | [s] | Stabilization Path Time Constant
Klr | 1 | [pu] | Current Input Factor
Ilr | 1 | [pu] | Current Input Referece
Vos | 1 | [1,2] | PSS Input Selector
Vel | 2 | [1,2,3] | Uel Input Selector
Vimin | -0.25 | [pu] | Controller Input Minimum
Vamin | -5 | [pu] | Controller Minimum Output
Vrmin | -4 | [pu] | Exciter Minimum Output
Vimax | 0.15 | [pu] | Controller Input Maximum
Vamax | 5 | [pu] | Controller Maximum Output
Vrmax | 4 | [pu] | Exciter Maximum Output

## G9
avr |  |  |  | TGOV1
Tr | 0.015 | [s] | Measurement Delay | T3 | 2 | [pu] | Turbine Delay Time Constant
Tb | 0.5 | [s] | Filter 1st Delay Time Constant | T2 | 1 | [pu] | Turbine Derivative Time Constant
Tc | 0.1 | [s] | Filter 1st Derivative Time Constant | At | 1 | [pu] | Turbine power coefficient
Tb1 | 0.5 | [s] | Filter 2nd Delay Time Constant | Dt | 0 | [pu] | Frictional Losses Factor
Tc1 | 1 | [s] | Filter 2nd Derivative Time Constant | R | 0.05 | [pu] | Controller Droop
Ka | 150 | [pu] | Controller Gain | T1 | 0.2 | [s] | Governor Time Constant
Ta | 0.05 | [s] | Controller Time Constant | PN | 0 | [Mw] | Turbine Rated Power(=0->PN=Pgnn)
Kc | 0.01 | [pu] | Current Limiter Factor | Vmin | 0 | [pu] | Minimum Gate Limit
Kf | 0.01 | [pu] | Stabilization Path Gain | Vmax | 1 | [pu] | Maximum Gate Limit
Tf | 1.2 | [s] | Stabilization Path Time Constant
Klr | 1 | [pu] | Current Input Factor
Ilr | 1 | [pu] | Current Input Referece | STAB1
Vos | 1 | [1,2] | PSS Input Selector | K | 223.6363 | [pu] | Stabilizer Gain
Vel | 2 | [1,2,3] | Uel Input Selector | T | 6.9373 | [s] | Washout integrate time constant
Vimin | -0.25 | [pu] | Controller Input Minimum | T2 | 2.7011 | [s] | Second Lead/Lag derivative time constant
Vamin | -5 | [pu] | Controller Minimum Output | T4 | 0.48676 | [s] | Second Lead/Lag delay time constant
Vrmin | -4 | [pu] | Exciter Minimum Output | T1 | 0.46542 | [s] | First Lead/Lag derivative time constant
Vimax | 0.15 | [pu] | Controller Input Maximum | T3 | 1.829 | [s] | First Lead/Lag delay time constant
Vamax | 5 | [pu] | Controller Maximum Output | HLIM | 0.03 | [pu] | Signal pss maximum
Vrmax | 4 | [pu] | Exciter Maximum Output